DAIKIN LXE10F

Unit BMOU9777781 Model: LX10F15A2 and with Set Temp of -18.0C.

1. Thanks for the feedback.

2. There are two possibilities, one is RA sensor faults and another possible unit under Quest mode.

3. Go to “Optional Function” Menu and then scroll down to Quest Function then change to OFF position.

4. Do Sensor Calibration test, first go to “Manual Check” Menu, select “All Sensor Calibration”.

5. Once done, Do provide the SS, RS, DSS and DRS Temp reading for our reference after 10minutes test.

Compressor NOT working and Temp out of Range

Unit FSCU5727183 Model: LX10F11B3NH and with Set Temp of -25.0C.

1. Thanks for the efforts in repairing the unit.

2. Based on RA -14.7C and if ambient temp is +20.0C; unit discharge manifold pressure or HPT display should be 1100Kpa to 1150Kpa.

3. Before gas release or top up, do assist to compare discharge manifold pressure with HPT displays. Are both discharge pressure the same? If different, possibly HPT PN: 158795J defective.

4. Do ensure EIS temp readings is cooler than EOS temp, if not compressor body will heavily frost-up and compressor body temp or DCHS display should be +70C to +98.0C. If these 2readings are NOT match, do provide us parameter values.

5. Do find attached parameter sample and provide data, if compressor In operation. Due to compressor NOT working; if can’t know actual faults. Is there alarm activation?

6. Do assist to reset defrost timer 99hourly for any frozen setting; unit is programmed will auto defrost every 4hourly if unit is out of range.

7. Based on parameter given, it look like Compressor not working?

8. Is anyone of phase Contactor energies? If no, do check input 3phase power input, phase contactors resistance or any fuses blown.

9. In case, HPT and discharge manifold pressure is different and No spare HPT. Do temporary isolate HPT wires and based on manifold gauge pressure to operate the unit.

10. May try to Operate under Emergency Mode, if Controller Failure.